## Slide 1: EV T&D Forecasting: Two Approaches
John Walkington
2024 AEIC & WLRA Conference
October 7-9, 2024

## Slide 2: top-down and Bottom-up methods are different approaches to answer the same questions
How much EV adoption can we expect in different parts of a utility’s service territory?
What customer characteristics influence EV adoption?
What will be the impact of increasing EV adoption on the T&D system?

## Slide 3: Why is being familiar with two methods useful?
Different data requirements for each method
  In instances where customer-level EV adoption data is not available, top-down methods can provide useful forecasts with publicly available inputs (DMV registration data, tax assessor property data)
  In instances where customer-level EV adoption data is available, bottom-up methods can provide more detailed results (more granular forecasts, an assessment of the “typical” EV adopter profile)
Each method is useful in different contexts
  Top-down methods are useful for long-term T&D planning, especially over broad service areas
  Bottom-up methods can be useful for more granular T&D planning and can also provide useful insights to improve EV program offerings

## Slide 4: Bottom-up EV T&D forecasting: Examples from the central Hudson gas & Electric Distribution system implementation plan

## Slide 5: The basics: What is a propensity score?
Starting point (coefficient)
Helps estimate adoption probability and distinguish early/late adopters
Homeowner
Home owner
Incentive amount
Has solar
Home value
Location
Age of home
Larger House
Larger House
Incentive Amount
Has solar
Home value
Location
Age of home
Each premise/site gets a different score based on their characteristics and how they correlate with adoption

## Slide 6: DER adoption (Propensity) Modeling Methodology
Analyze customers who have and have not adopted the DER in question
Explore relationship of all possible predictive variables for DER adoption
  Correlation
  Plots
  Bivariate regressions
Identify the key predictors of adoption
Identify non-linear patterns
Split data into training/testing data
Train Model on predictive features
  XG Boost
  Model identifies what best predicts the outcome
  Captures non-linear and linear relationships
  The models iterates and learns, improving with each iteration
Models are assessed using the testing data
Predict likelihood of adoption (today) for each premise and DER – aka propensity score
The predictions factor in customer specific information and helps us distinguish early adopters from late adopters
The propensity scores are scaled so the sum of the adoption probabilities for each year equals the system level forecast (Calibration)
When aggregated by feeder, it provides the expected adoption by year and DER for each feeder
STEP 1:
Exploratory Data Analysis
STEP 2:
Machine Learning Model
STEP 3:
Apply to all Customers

## Slide 7: Methods for Evaluating Model Outputs
Hashed Line represents a base case of randomly classifying adoptions (50/50 chance to get the right assignment)
The yellow line represents the Receiver Operating Characteristic Curve
Feature importances are another method to evaluate model inputs and see what variables were important in the prediction
These do not indicate why a feature is important, that is up to the bivariate analysis
Comparing propensity scores with actual adopters allows the evaluation of how well the model scores probabilities for a given site

## Slide 8: Key facts
Vehicle Class | Gas | Diesel | Hybrid | Electric only | PHEV | Other | Total
LDV | 538,448 | 9,898 | 13,604 | 4,030 | 2,791 | 1,081 | 569,852
MHDV | 7,571 | 17,474 | 1 | 4 | 0 | 379 | 25,429
BUSES | 158 | 1,324 | 0 | 0 | 0 | 125 | 1,607
Total | 546,177 | 28,696 | 13,605 | 4,034 | 2,791 | 1,585 | 596,888
EVs are small share of total vehicles currently
They are growing as share new vehicle sales
Data Used to Explore Adoption patterns
NYSERDA rebate data from 2018 forward
Linked customers to Central Hudson accounts, billing data and property data
2,868 sites linked
Used to explore patterns of what does and does not influence adoption
Source data: https://data.ny.gov/Transportation/Vehicle-Snowmobile-and-Boat-Registrations/w4pv-hbkt/data with mapping to CH territory by DSA

## Slide 9: Understanding the relationship between Ev adoption and customer characteristics ( 1 of 2)
Income Bins
Gross Annual Usage
House Size
Square Ft
Bins
Zone (Location)
*Important to note that all electric usage values (Annual/Winter/Summer usage and Cooling/Base load) are usage before adoption of DERs. Usage for Solar adopters was calculated as Gross Annual Usage with solar production added in.

## Slide 10: Understanding the relationship between Ev adoption and customer characteristics (2 of 2)
Home
Type
Home Year Built Bins
Has
Solar
Owner
Occupied

## Slide 11: We run each of potential predictors to identify what best predicts adoption on its own, then combine predictive variables into a multivariate model
variable name | variable type | AUC | F1 | recall | precision | sensitivity | specificity | accuracy
win_usage_bins100 | categorical | 0.665 | 0.656 | 0.729 | 0.596 | 0.729 | 0.506 | 0.617
income_bins | categorical | 0.651 | 0.579 | 0.526 | 0.643 | 0.526 | 0.708 | 0.617
gross_ann_usage_bins100 | categorical | 0.645 | 0.617 | 0.639 | 0.597 | 0.639 | 0.570 | 0.604
sum_usage_bins100 | categorical | 0.641 | 0.576 | 0.546 | 0.609 | 0.546 | 0.650 | 0.598
ann_base_load_bins100 | categorical | 0.631 | 0.599 | 0.608 | 0.591 | 0.608 | 0.579 | 0.593
ln_gross_ann_usage | continuous | 0.626 | 0.615 | 0.659 | 0.576 | 0.659 | 0.515 | 0.587
gross_ann_usage | continuous | 0.626 | 0.536 | 0.479 | 0.607 | 0.479 | 0.690 | 0.584
sqft_bins10 | categorical | 0.607 | 0.610 | 0.659 | 0.569 | 0.659 | 0.500 | 0.580
ann_cooling_kwh_bins100 | categorical | 0.605 | 0.550 | 0.521 | 0.583 | 0.521 | 0.627 | 0.574
sqft | continuous | 0.601 | 0.521 | 0.476 | 0.576 | 0.476 | 0.649 | 0.563
zone | categorical | 0.593 | 0.619 | 0.700 | 0.555 | 0.700 | 0.439 | 0.569
ln_win_usage | continuous | 0.591 | 0.642 | 0.770 | 0.551 | 0.770 | 0.373 | 0.571
win_usage | continuous | 0.591 | 0.510 | 0.446 | 0.596 | 0.446 | 0.698 | 0.572
lotsize | continuous | 0.586 | 0.293 | 0.194 | 0.594 | 0.194 | 0.868 | 0.531
rate_cd | categorical | 0.584 | 0.391 | 0.284 | 0.627 | 0.284 | 0.832 | 0.558
yearbuilt_bins10 | categorical | 0.580 | 0.499 | 0.432 | 0.590 | 0.432 | 0.699 | 0.566
bldg_type | categorical | 0.573 | 0.676 | 0.902 | 0.540 | 0.902 | 0.231 | 0.567
has_solar | categorical | 0.571 | 0.299 | 0.183 | 0.814 | 0.183 | 0.958 | 0.571
der303008_res_solar | categorical | 0.570 | 0.297 | 0.182 | 0.813 | 0.182 | 0.958 | 0.570
yearbuilt | continuous | 0.568 | 0.586 | 0.649 | 0.535 | 0.649 | 0.436 | 0.543
ann_cooling_kwh | continuous | 0.551 | 0.456 | 0.388 | 0.552 | 0.388 | 0.685 | 0.537
shoulder_usage | continuous | 0.546 | 0.477 | 0.425 | 0.543 | 0.425 | 0.642 | 0.533
comparison_gross_ann_usage_eui_bybldg_type_100 | continuous | 0.546 | 0.536 | 0.544 | 0.529 | 0.544 | 0.515 | 0.530
owneroccupied | categorical | 0.543 | 0.629 | 0.776 | 0.529 | 0.776 | 0.311 | 0.543
ann_base_load | continuous | 0.535 | 0.499 | 0.455 | 0.553 | 0.455 | 0.632 | 0.544
der403010_res_hp | categorical | 0.522 | 0.112 | 0.060 | 0.789 | 0.060 | 0.984 | 0.522
sum_usage | continuous | 0.514 | 0.477 | 0.433 | 0.533 | 0.433 | 0.620 | 0.526
der103003_res_battery | categorical | 0.505 | 0.025 | 0.013 | 0.829 | 0.013 | 0.997 | 0.505
der503012_res_hpwh | categorical | 0.504 | 0.025 | 0.013 | 0.739 | 0.013 | 0.995 | 0.504
gas | categorical | 0.501 | 0.606 | 0.767 | 0.500 | 0.767 | 0.235 | 0.501
other_der_flag_Non-Residential | categorical | 0.500 | 0.000 | 0.000 | 1.000 | 0.000 | 1.000 | 0.500
other_der_flag_Residential | categorical | 0.500 | 0.000 | 0.000 | 1.000 | 0.000 | 1.000 | 0.500
ln_sum_usage | continuous | 0.486 | 0.362 | 0.278 | 0.519 | 0.278 | 0.742 | 0.510

## Slide 12: Use best multivariate model to predict propensity scores for each location
Substation Penetration

## Slide 13: After producing propensities, calibrate to overall forecast
We use an in-house Python function to calibrate our EV categories like three separate DERs
  The function calibrates an adoption S-curve according to every location’s propensity while all adding up to the top line forecast
  Higher propensity locations will have a quicker uptake in the beginning, but slow down in later years of the forecast (and vice-versa)

## Slide 14: Top-Down EV T&D forecasting: examples from the Pennsylvania Statewide evaluator’s Avoided T&D Cost Study

## Slide 15: Data sources and overall strategy
PJM EV forecast
  Energy consumption (GWh)
  Vehicle counts
  MHDV load shape
NREL EV load shapes
  LDV home load shape
  LDV public load shape
Locations of public chargers (AFDC)
Feeder geometry (from utilities)
EV registration data (from PennDOT)
Commercial property data (SMR)
Data Sources
Develop top-line forecast for EV GWh for 15 years
  Use PJM as starting point, modify to reflect PA SWE territory
Split forecast into three main EV categories: LDV at-home charging, LDV public charging, and MHDV
Estimate adoption propensity for each EV category at the feeder level
Calibrate feeder-level EV adoption to overall forecast
Estimate hourly EV loads for each category by year and feeder

## Slide 16: Steps 1+2: develop top-line ev GWh forecast, split into each EV CATEGORY
PJM published EV usage estimates and counts for each zone for 2024-2039
Some zones map 1:1 to utilities; for those that don’t, estimate multiplier based on ratio of utility peak to zone peak
Use vehicle miles traveled and efficiency assumptions for LDV and MHDV to determine LDV/MHDV split
Divide LDV GWh into at-home and public charging proportional to the area under the stacked load shape

## Slide 17: Steps 1+2: develop top-line ev GWh forecast, split into each EV CATEGORY
Year | PA SWE Forecast (GWh) |  |  | Total | PA SWE Forecast (% of total) |  | 
 | LDV At-Home | LDV Public | MHDV |  | LDV At-Home | LDV Public | MHDV
2024 | 169 | 52 | 158 | 379 | 44.5% | 13.8% | 41.7%
2025 | 395 | 122 | 354 | 870 | 45.3% | 14.0% | 40.7%
2026 | 688 | 212 | 643 | 1,543 | 44.6% | 13.8% | 41.7%
2027 | 1,002 | 310 | 971 | 2,283 | 43.9% | 13.6% | 42.5%
2028 | 1,327 | 410 | 1,337 | 3,074 | 43.2% | 13.3% | 43.5%
2029 | 1,695 | 524 | 1,771 | 3,989 | 42.5% | 13.1% | 44.4%
2030 | 2,096 | 648 | 2,223 | 4,966 | 42.2% | 13.0% | 44.8%
2031 | 2,594 | 802 | 2,767 | 6,162 | 42.1% | 13.0% | 44.9%
2032 | 3,168 | 979 | 3,392 | 7,539 | 42.0% | 13.0% | 45.0%
2033 | 3,766 | 1,164 | 4,056 | 8,986 | 41.9% | 13.0% | 45.1%
2034 | 4,457 | 1,377 | 4,833 | 10,667 | 41.8% | 12.9% | 45.3%
2035 | 5,227 | 1,615 | 5,721 | 12,564 | 41.6% | 12.9% | 45.5%
2036 | 6,037 | 1,865 | 6,654 | 14,556 | 41.5% | 12.8% | 45.7%
2037 | 6,849 | 2,116 | 7,593 | 16,558 | 41.4% | 12.8% | 45.9%
2038 | 7,684 | 2,374 | 8,558 | 18,616 | 41.3% | 12.8% | 46.0%
2039 | 8,635 | 2,668 | 9,668 | 20,972 | 41.2% | 12.7% | 46.1%

## Slide 18: Step 3: Estimate Feeder propensities for each EV type
After mapping feeders to zip codes, zip code counts of EV and regular vehicle registrations are allocated in proportion to feeder peaks within a zip code
Feeder-level “EV share” is used as a propensity score
LDV Home Charging
LDV Work/Public Charging
MHDV Charging
After mapping public charging stations to feeders, the proportion at each feeder of the total statewide ports is used as a propensity score. For example, if 2 ports are at one feeder and there are 2000 ports in PA, p-score = .001
For feeders without chargers, give them a nonzero propensity much lower than the feeders with chargers—more public charging locations will pop up eventually, but existing charging locations will take off first
After mapping all commercial properties in PA to feeders, filter to industries that use medium- or heavy-duty vehicles and have potential to electrify (transportation, public schools, mining, etc.)
Use the proportion at each feeder of total statewide commercial square footage as a propensity score (similar to LDV public)
For feeders without commercial square footage, use a nonzero propensity that is much lower—these locations will grow eventually but commercial corridors will grow faster and earlier

## Slide 19: Step 4: Calibrate feeder propensities to overall forecast
We can use a DSA function to calibrate our EV categories like three separate DERs
  The function calibrates an adoption S-curve according to every location’s propensity while all adding up to the top line forecast

## Slide 20: Step 5: Estimate hourly ev loads by year and feeder
The calibration function outputs annual MWh by feeder by year for each EV type
To estimate hourly loads, divide by 365 and multiply by normalized load shape (all hours add to 1)
Each EV type gets multiplied by its own load shape:
After creating hourly loads for each EV type, collapse to the feeder-year level
Each feeder-year shape will be a linear function of these three load shapes
LDV Home Charging
LDV Work/Public Charging
MHDV Charging

## Slide 21: Example 2025 and 2030 hourly load for a Duquesne feeder
Ex

## Slide 22: Distribution of ev load across Duquesne

## Slide 23: Distribution of ev load across Firstenergy

## Slide 24: Distribution of ev load across PECO

## Slide 25: Distribution of ev load across PPL

## Slide 26: knowing both methods makes for a flexible analysis toolkit
Bottom-up methods have pros and cons:
  Provides information on characteristics that are most likely to influence EV adoption, which can be leveraged for EV program marketing and decision-making
  Requires data that not all utilities maintain, such as customer-level EV adoption/rebate data and customer characteristics (home type, income estimates, etc.)
Top-down methods have pros and cons :
  Can be used for EV categories where adoption is not yet widespread enough to build a propensity model, such as medium- and heavy-duty EV’s (MHDV)
  Less detailed data is required to create a model
Which method to use will depend on the utilities’ research questions, the project context, and the data available.
  The two methods are not incompatible and can be used in conjunction with one another as long as the outputs of each approach are calibrated.

## Slide 27: Questions?
John Walkington
Consultant
Demand Side Analytics
jwalkington@demandsideanalytics.com